## Slide 1: Infiltration and Inflow Control Massachusetts Regulatory Framework
Kevin Brander
Bureau of Water Resources
Scott Haynes, PE, BCEE
Paul Batman, PE

## Slide 2: Overview
  Sanitary Sewer Overflows
    Public Health Problem!!
  Sewer Authorities in MA
    Must have program to
    remove Infiltration/Inflow
  MassDEP issued updated I/I Guidance in May 2017

## Slide 3: SSO Problems
Since 2006 in MA Northeast Region…
  > 3,800 events in 70 communities

## Slide 4: SSO Volumes
But……….looking at SSO volume by cause…
Over 650 million gallons in SSO!

## Slide 5: SSO’s create Public Health Risks!!

## Slide 6: Infiltration
groundwater entering sewers, service laterals, or manholes through defects and joints in the system.

## Slide 7: Inflow
Stormwater or surface waters entering the sewer system through drains, catch basins, roof leaders, manhole covers, and flows from sump pumps connected to the sewer.
Over 19,000 disconnected in Boston
So far!!

## Slide 8: Regulatory Requirements
  Regulatory Requirements 314 CMR 12.04(2):
  All MA Sewer Authorities must develop and implement an ongoing I/I program:
    Identify and eliminate “excessive” Inflow/Infiltration sources
    Focus on inflow sources
    Phased evaluation of sewer system consistent with MassDEP Guidance
    I/I mitigation for new connections for CSO and tributary systems

## Slide 9: Regulatory Requirements - Mitigation
For CSO/tributary systems:
  4:1 I/I mitigation requirement for all
  new connections > 15,000 gpd
  Up to sewer authority to establish program, including:
    Design flows
    Direct removals or Fees
    NepRWA Sewer Banking guidance at https://www.neponset.org/projects/publications/

## Slide 10: Regulatory Requirements
  By December 2017 submit I/I Analysis:
  To address excessive I/I based on MassDEP’s Guidelines for Performing I/I Analyses and Sewer System Evaluation Surveys
  Assess the risk for sanitary sewer overflows for the 5-year, 24 hour storm
  Many municipalities well into implementation phase!

## Slide 12: Infiltration and Inflow Program Guidance
Revised MassDEP I/I Guidance (1993 2017)
  NEWEA Collection System Committee/Advisory Group
    held meetings, conference calls
  Notice for Public Comment in 8/24/2016 Environmental Monitor
  Comments from municipal groups, consultants
  Final Guidance issued May 2017
    http://www.mass.gov/eea/agencies/massdep/water/wastewater/sewer-systems.html#5

## Slide 13: 2017 Guidance – I/I Abatement Programs
Guidance establishes four step approach:
  Infiltration and Inflow Analysis – by 12/31/2017
  Sewer System Evaluation Survey
  Sewer System Rehabilitation
  Post-Construction Monitoring
  Alternative approaches may
  be proposed!

## Slide 14: Elements of I/I Analysis
Inventory of Sewer System/GIS
Flow Monitoring (3/1 – 6/30)
Manhole inspections (10%)
GW monitoring
Rainfall Monitoring
    (min 2 gauges, 1 per 3-4 mi2)
Flow Data Analysis:
    Sanitary
    Infiltration (peak and average)
    Inflow (correlating to storm size)

## Slide 15: Elements of I/I Analysis SSO Analysis – 5 Year Storm
National Oceanic and Atmospheric Administration Atlas 14, Volume 10
    5 Year 24-hour event:
          4.61 inches of rain
          Peak intensity of 0.73 in/hr
Wet Weather SSO event assessment
    Review wet weather SSO event history vs. storm events

## Slide 16: I/I Analysis Report
I/I Analysis Report Recommendations:
  Develop Sewer System Evaluation Survey (SSES) Program based on flow monitoring findings ……
    Infiltration: Prioritize subareas with highest infiltration for further investigation – initially those > 4,000 gpdim
    Inflow: Further investigation of subareas comprising 80% of total inflow to system

## Slide 17: Sewer System Evaluation Survey
SSES: I/I investigations to identify Specific Sources
    Infiltration: Flow isolation Inflow: Smoke testing, dye
    CCTV, manhole inspections testing, property inspections
    SSES targets removal of Excessive I/I

## Slide 18: 2016 Guidance – When is I/I Excessive?
“Excessive” I/I:
  Contributes/causes SSO’s for events up to 5 year storm
  Infiltration which can be cost-effectively removed from the sewer system
  Public and private inflow sources, unless technically infeasible or cost-prohibitive

## Slide 19: Sewer System Evaluation Survey
Cost-Effectiveness Evaluation (CEA):
    Infiltration Sources: Evaluate costs to Transport/Treat infiltration vs. Removal Costs
    >
    Typical Fixes: pipe and MH lining, spot repairs, grouting
    Inflow Sources: No CEA! Remove unless technically infeasible or cost-prohibitive

## Slide 20: Cost-Effective?
CEA hasn’t yielded effective I/I removal in some cases
  Migration of infiltration
  Limited design life of fixes
Need to look at
    Design life of fixes
    Removal assumptions
      (50 % peak infiltration)
  Collecting post-construction data

## Slide 21: In-Field Adjustments

## Slide 22: Private Inflow Removal
Sewer regulations must prohibit connection of inflow sources
Can have BIG impact, but often avoided:
    Sump pumps
    Roof leaders
    drains
Requires property inspections

## Slide 23: Private Inflow Removal Technically Infeasible or Cost-Prohibitive?
Factors:
  Private inflow causing/contributing to SSOs?
  Costs to utility/property owner for removal
  Is there a reasonably feasible alternative
  discharge location?
  Creation of nuisance conditions
  DEP: If frequent SSO’s, rigorous private inflow identification/removal will be required!

## Slide 24: SSES Report
Report/Recommendations:
          List of rehabilitation work
          I/I estimated to be removed
          Cost
          Schedule for design and construction
          Post Construction Monitoring
              12, 18, 24 month warranties

## Slide 25: Funding Sources
SRF Funds Are Available – 2% Loan Program
  SRF funds studies and construction work
  Competitive process
Massachusetts Water Resources Authority
  Boston metro/area, 43 communities
  I/I Community Support Program – 75% grants!
  Ten phase of distributions so far, over the past 15 years

## Slide 26: It Takes Two
Notes: WSSC Trunk Sewer Inspections

## Slide 27: ArcGIS Collector
Notes: Completely Customizable
Use it for any sewer field activities
manhole inspections
smoke testing
tracking CCTV inspections
Use built-in GPS or connect an external unit for greater accuracy
ESRI supported

## Slide 28: WSSC Trunk Sewer Manhole Inspections
Notes: Real time tracking of completed inspections – great for multiple teams operating in the same area

## Slide 29: WSSC Trunk Sewer Manhole Inspections

## Slide 30: WSSC Trunk Sewer Manhole Inspections
Notes: Field teams:
  Collect the data
  Provide feedback on the tools (constant improvement)
Office Support:
  Prep GIS Mapping
  QA/QC Reviews and feedback to field teams
  Prep Deliverables
Trade roles:
  Have QA reviewers do a some inspections
  Have inspectors do some QA reviews

## Slide 31
Features/Benefits
ArcGIS Collector
ESRI Application
Integrated GPS
Cloud Data
Real-time Tracking
Multiple Users
Direct Data Entry
Link Photos and Videos
Notes: ArcCollector - No hand notes, GPS locating for data entry - better accuracy, Less steps for error data entry/transfer, Mulitple users, Immediate entry to , Offline vs. online mode (cellular connection, battery life)
Daily data backup (or more) (manually if not online) - or constant backup by connection to remote server (cellular data plan)

## Slide 32
Features/Benefits
Challenges
ESRI Application
Integrated GPS
Cloud Data
Real-time Tracking
Multiple Users
Direct Data Entry
Link Photos and Videos
Battery Life
Tree Cover
Cellular Coverage
Screen Brightness
ArcGIS Collector
Notes: ArcCollector - No hand notes, GPS locating for data entry - better accuracy, Less steps for error data entry/transfer, Mulitple users, Immediate entry to , Offline vs. online mode (cellular connection, battery life)
Daily data backup (or more) (manually if not online) - or constant backup by connection to remote server (cellular data plan)

## Slide 33: Questions?
Kevin Brander, PE
MassDEP/NERO
(978) 694-3236
Kevin.Brander@state.ma.us
Scott Haynes, PE, BCEE
Scott.Haynes@arcadis.com
Paul Batman, PE
Paul.Batman@arcadis.com